# ANNEX II + III:	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

Contract title: Supply of Equipment for Renovation at Hotel Simsek in Merkez, Edirne, Türkiye	                                                                                     p 1/3

Publication reference: BGTR0300155-PP2-SUP-01/LOT 1

LOT 1: Elevator motor

Columns 1-2 should be completed by the contracting authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the contracting authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words ‘compliant’ or ‘yes’ are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

| 1. Item number | 2. Specifications required | 3. Specifications offered | 4. Notes, remarks, ref to documentation | 5. Evaluation committee’s notes |
| --- | --- | --- | --- | --- |
| 1 | Elevator motor |  |  |  |
| 1.1 | Elevator motor The current situation: 5 stops + 1 ground floor = 6 stops, 1.00 m/s speed, Class I elevator (Elevators designed for transporting people). Stepless speed, Rated load: 630 kg. Dimensions: Unit. Load capacity (Rated load): 630 kg, Shaft (horizontal section) dimensions: 2000x2100 mm (width x depth), Cabin horizontal section dimensions: 1100x1400 mm (width x depth), If the dimensions in TS ISO 8100-30 cannot be provided, the cabin area will be 1.45 - 1.66 m2 according to TS EN 81-20. Entrance width: 900 mm, Entrance height: min. 2000 mm according to TS EN 81-20. Note: Arrangements will be made inside the cabin to accommodate disabled users. The provisions of Article 45 of the Planned Areas Type Zoning Regulation will be taken into consideration when calculating door width and cabin area. New Engine Type and Efficiency Motor Type: New elevator drive system, energy efficient and gearless motor system. Energy Efficiency: The motor must have the highest possible energy efficiency rating. |  |  |  |
|  | Engine Assembly and Disassembly Disassembly: The disassembly of the existing motor will be carried out using methods that do not damage the structural integrity of the existing building and in full compliance with occupational safety regulations. The resulting waste will be disposed of by the contractor in accordance with environmental regulations. Assembly Parts: All drive components that need to be replaced along with the motor must be compatible with the new system, CE certified, and comply with international standards. Warranty and Service Terms Warranty Period: A full warranty of at least two years must be provided for the new motor, driver, and installation workmanship. Authorized Service: At the end of the work, the contractor must provide a maintenance contract with an authorized service provider that complies with the Elevator Operation and Maintenance Regulation and possesses a TSE Service Qualification Certificate. Documentation: At the end of the work, there must be no issues preventing the registration of the elevator, and obtaining the Blue/Green Information Label must be the contractor's responsibility. |  |  |  |