# ANNEX II + III:	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

# Contract title: Supply of Equipment for Renovation at Hotel Simsek	p 1 / 4

Publication reference: BGTR0300155-PP2-SUP-01/LOT 3

LOT 3: Air conditioning system and lighting

Columns 1-2 should be completed by the contracting authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the contracting authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words ‘compliant’ or ‘yes’ are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

| 1. Item number | 2. Specifications required | 3. Specifications offered | 4. Notes, remarks, ref to documentation | 5. Evaluation committee’s notes |
| --- | --- | --- | --- | --- |
| 3 | Air conditioning system and lighting. |  |  |  |
| 3.1. | 37 new air conditioners installed in the rooms, 4 for the restaurant, and 2 for the breakfast room. Cooling capacity (nominal): 3.3 kW, Heating capacity (nominal): 3.5 kW, Wall-mounted split air conditioners: Split Air Conditioning Units: (Quantity: Unit) (TS 7936 EN 60335-2-40, TS EN 814-3, TS EN 14511-4) On-site supply, installation, and commissioning of a split-type air conditioner with the following specifications: equipped with a DC Inverter compressor and heat-pump functionality; Energy Class A for both cooling and heating consumption; featuring memory protection against power outages with an auto-restart function at the previous settings; capable of independent dehumidification (reheat dehumidification) without altering ambient temperature; operating temperature range between +18°C and +40°C; minimum seasonal energy efficiency ratings of SEER 5.8 and SCOP 4.0; including indoor and outdoor units, inter-unit copper piping, drainage lines, and electrical wiring. Cooling capacity (nominal): 12 kW, Heating capacity (nominal): 12 kW, Room type air conditioners: Room type split air conditioning units: (Quantity: Unit) (TS 7936 EN 60335-2-40, TS EN 814-3, TS EN 14511-4) On-site supply, installation, and commissioning of a floor-standing split-type air conditioner with the following specifications: equipped with a DC Inverter compressor and heat-pump functionality; Energy Efficiency Class A for both cooling and heating; featuring memory protection against power outages with an auto-restart function at previous settings; capable of independent dehumidification without altering ambient temperature; operating temperature range between +18°C and +40°C; minimum seasonal energy efficiency ratings of SEER 5.8 and SCOP 4.0; including indoor and outdoor units, inter-unit copper piping, drainage lines, electrical wiring, and all necessary hardware. |  |  |  |
| 3.2. | Installation of new lighting fixtures in 53 rooms - min. 6-watt LED bulb, electrical system renovation. The lighting units to be used throughout the facility must have a minimum power of 6 Watts and be fully compatible with existing fixtures. To ensure color consistency across all rooms, a fixed color temperature of either 3000K or 4000K must be preferred. The selected products shall be CE certified, featuring internal drivers capable of flicker-free operation under 220-240V mains voltage. A total of 53 bulbs will be delivered in their original packaging, undamaged, following sample approval. These bulbs must be covered by a minimum 2-year replacement guarantee against manufacturing defects. |  |  |  |