# ANNEX II + III:	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

Contract title: Supply of Equipment for Renovation at Hotel Simsek in Merkez, Edirne, Türkiye	                                                                                    p 1 / 7

Publication reference: BGTR0300155-PP2-SUP-01/LOT 4

LOT 4: Simple renovation work in the boiler room

Columns 1-2 should be completed by the contracting authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the contracting authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words ‘compliant’ or ‘yes’ are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

| 1. Item number | 2. Specifications required | 3. Specifications offered | 4. Notes, remarks, ref to documentation | 5. Evaluation committee’s notes |
| --- | --- | --- | --- | --- |
| 4 | Simple renovation work in the boiler room. |  |  |  |
| 4.1. | Group 1 - Renewal of 1000L water heater (boiler) and installation parts: 1000 liters capacity; Lower coil: 1340 L/h (10.0 kPa); Upper coil: 600 L/h (1.5 kPa). Includes all installation labor, mounting accessories, and necessary materials. Double Steel Coil Vertical Boiler A vertically manufactured boiler designed for an operating pressure of 10 bar, with coil temperature conditions of 90/70 °C and domestic hot water temperature conditions of 10/60 °C. The minimum domestic hot water flow rates for the lower and upper coils and the maximum flow resistance on the coil side shall be specified. All other features shall be the same as those of a single-coil vertical boiler. The boiler shall be manufactured in a vertical configuration in compliance with TS EN 13445-3, TS EN 12897, and TS 736 standards, and shall be equipped with inspection and cleaning manholes. It shall include a suitable connection port for the installation of an electric heater if required. The internal surface of the tank and the external surface of the coil shall be coated with enamel of at least 180 microns thickness, while the external surface of the tank shall be enamel-coated or painted with two layers of anti-corrosion paint to prevent external corrosion. The tank body shall withstand a test pressure equal to 1.3 times the operating pressure of 10 bar. The coil shall be manufactured from pipes in accordance with TS ISO 1129 standards, and the system shall be equipped with a magnesium anode with a weight of 200 g/m² per unit internal surface area, or an impressed current anode. In the case of a 316-grade stainless steel coil, the coil and impressed current anode shall comply with TS 10380 and the Pressure Equipment Directive (2014/68/EU). The boiler body shall be insulated with HCFC-free rigid polyurethane foam with a minimum density of 40 kg/m³ and a minimum thickness of 50 mm, or alternatively with polyurethane foam having a minimum density of 15 kg/m³ and a minimum thickness of 80 mm. The outer casing shall be made of galvanized sheet metal or sheet metal coated with at least 50 microns of electrostatic powder paint, or an equivalent protective outer cladding. The scope includes on-site supply, connection to the installation, and delivery of the boiler in fully operational condition. |  |  |  |
| 4.2. | Seam-welded black steel pipes (welded installation inside the building, including 25% fittings): renewal of one set of heating pipes and insulation of all heating pipes together with the hot water boiler insulation. Steel Pipes: Supply and installation on site, including workmanship, of steel pipes placed on the market with the CE Conformity marking in compliance with the Construction Products Regulation (EU) No 305/2011 and the Pressure Equipment Directive (2014/68/EU), installed and connected in accordance with the relevant specifications and project requirements, excluding the cost of red lead primer and paint. |  |  |  |
| 4.3. | Replacement of 2 heating circulation pumps and 1 boiler heating pump with variable-speed (frequency converter–controlled) circulation pumps, having a flow rate of 9–12 m³/h and a head of 3–5 mSS. The pumps shall be wet-rotor circulation pumps suitable for installation on straight piping. Variable-Speed (Frequency Converter–Controlled) Wet-Rotor Circulation Pump: In accordance with TS EN 16297-1/2/3, the wet-rotor circulation pumps suitable for installation on straight piping shall comply with the Ministry of Science, Industry and Technology’s Regulation on Ecodesign Requirements for Independent and Glandless Circulation Pumps Integrated into Products, with an Energy Efficiency Index (EEI) < 0.23, and PN10 pressure class. The motor shall be self-protected against blockage, overload, and overheating, and shall be equipped with an internal or external frequency converter. The pumps shall be compatible with Ap-c and Ap-V control modes, and the head and fault signal information shall be viewable directly on the unit without the need for additional equipment. The system shall operate with automatic regulation, featuring an internal display that allows head adjustment in increments of up to 0.5 m. The pump body material shall be at least TS 552 EN 1561 / EN-GJL-200 (GG20), bearings shall be metal-impregnated carbon, the impeller shall be stainless steel or glass fiber–reinforced polypropylene, and the pump shaft shall be manufactured from material compliant with TS EN 10088-3. The pump enclosure protection class shall be at least IP44 or IPX4D, motor insulation class shall be at least Class F, and the operating temperature range for hot water circulation pumps shall be –10°C to +110°C in accordance with TF95 classification. |  |  |  |
|  | Note: 1- During pump selection and procurement, the point values specified in the approved application project shall be taken into account. 2- The ranges specified in the item descriptions indicate the pump operating areas based on the approximate cost.Flow Rate (m³/h): 9-12 / Head (mSS): 3-5, Variable Speed (Frequency Controlled) Circulation Pump: Wet-rotor in-line circulation pumps: Technical Specification: Variable Speed (Frequency Controlled) Wet-Rotor Circulation Pump: (TS EN 16297/1-2-3). Wet-rotor in-line circulation pumps shall have an Energy Efficiency Index of EEI < 0.23 in accordance with the "Ecodesign requirements for glandless standalone and product-integrated circulators" by the Ministry of Science, Industry and Technology. The pumps shall be of PN10 pressure class, with motors self-protected against blockage, excessive strain, and overheating. They must be equipped with internal or external frequency converters, suitable for and control modes. Pump head and fault signal information must be displayable on the unit without the need for additional equipment. The system shall operate with an automatic regulation arrangement allowing the head to be adjusted via an integrated screen at maximum intervals of 0.5 m. The pump body material shall be at least TS 552 EN 1561 / EN-GJL 200 (GG20), bearings made of metal-impregnated carbon, impeller made of stainless steel or glass-fiber reinforced polypropylene, and the pump shaft manufactured from a material compliant with TS EN 10088-3. The insulation class shall be at least IP44 or IPX4D, the motor protection class at least Class F, and the operating temperature range shall be -10°C / +110°C according to the hot water circulation pumps class TF95. The scope includes the on-site supply and installation of the wet-rotor circulation pump in working condition. Note: During pump selection and procurement, the point values specified in the approved application project shall be taken into account. |  |  |  |
| 4.4. | Renewal of Group 1 Hot Water Boiler: Wall-mounted gas-fired condensing boilers between 100 kW - 114.9 kW, compatible with natural gas and/or LPG, including installation labor. Technical Specification: Wall-Mounted Gas-Fired Condensing Boilers for Natural Gas and/or LPG (Unit: Pcs). The boilers shall be manufactured in accordance with the 2014/426/EU Gas Appliances Regulation, bearing the CE mark, and equipped in compliance with TS EN 656/A1, TS EN 15502-2-2, and TS EN 15502-2-1+A1 standards. The heat exchanger sections exposed to condensation shall be made of corrosion-resistant materials. The unit shall feature a premix type (full pre-mix) gas burner and a modulated fan. The system must be controlled by an electronic board capable of managing high and/or low-temperature heating circuits and the domestic hot water (boiler) circuit, performing combustion and gas-air modulation. It shall include safety equipment compatible with the control system and be suitable for connection to any of the hermetic flue types: B23, B23p, B33, C13, C33, C43, C53, or C83, with a condensate drain connection provided. For total system capacities exceeding 200 kW, an external neutralizer shall be added. Additionally, the boiler shall be equipped with internal or external control units featuring outdoor reset, indoor temperature control, domestic hot water temperature control, and weekly programming capabilities. The scope includes the on-site supply, installation, and commissioning of the wall-mounted boiler, including a pump set suitable for the internal or external capacity. Note: The device capacity shall be based on the output at 50°C / 30°C flow and return water temperatures. |  |  |  |